CLEANING AND DISINFECTING YOUR DRINKING WATER SMALL STORAGE TANK

Ensure all materials used for storage tanks are intended for the use of potable water. If materials not suitable for potable water contact are used, harmful chemicals such as heavy metals or hydrocarbons could leach into your drinking water. Storage tanks should be sealed and kept fly tight to prevent onsite contamination.

Delivered water should be potable (safe for human consumption) and obtained from an approved source. Surface water is continually susceptible to contamination from wild life, aquatic life, domesticated animals and humans. All surface water used for domestic use should be treated to ensure a safe supply. The water hauler is required to disinfect this water for your safety.

Storage tanks should be cleaned and disinfected at least twice a year (spring and fall). This is to remove algae (plant growth which produces bad tastes and odours), silt, and bacteria which may be harmful.

## PROCEDURES

- Drain water from tank.

- Physically scrub or pressure wash the interior walls to remove sediment and grime.

- Rinse the inside surfaces of tank with clean potable water. Drain wash water.

- Fill tank with clean potable water.

- Add the required amount of unscented household bleach to the water in the storage tank (see table below). Mix well.

- To disinfect the plumbing lines and fixtures, open all taps in distribution system until chlorine smell is apparent at each outlet. Close taps.

- Let chlorine solution sit in the water system for at least 12 hours. Do not consume this highly concentrated solution.

- Drain the water tank but not into a septic system or fish bearing stream.

- Refill with fresh potable water.

- Open valve to distribution lines. Run water from the taps until there is no smell of chlorine.

| Dosage of Household Bleach (~ 5% chlorine) required for the Cleaning and Disinfecting of Water Holding Tanks |
| --- |
| Tank Size | Amount of Household Bleach to obtain 50 ppm Chlorine |
| Litres | Imp. Gallons | mL | Imp. Ounces | Cups |
| 227 455 909 1137 2273 4546 6819 9092 11365 | 50 100 200 250 500 1000 1500 2000 2500 | 227 511 909 1136 (1.2 L) 2273 (2.3 L) 4546 (4.5 L) 6818 (6.8 L) 9091 (9.1 L) 11340 (11.5 L) | 8 18 32 40 80 160 240 320 400 | 1 2 4 5 10 20 30 40 50 |